## Slide 1
MHT4-20kW Master-Slave Paralleling Solution
www.solinteg.com
2023.5.9 V1.0

## Slide 2
Solution Introduction
The hybrid inverter has become a new trend that has gained popularity in recent years as a result of the rising energy problem and electricity rates. But due to its short emergence, the power range hasn't been enlarged to cover all kinds of scenarios, so in some cases, a parallel system is required to expand the system application diversity.
In a storage system with multiple Integ MHT hybrid inverters (≤10pcs), a parallel solution is required to manage and control all inverters’ operation modes, energy supply and use. Solinteg Hybrid inverter supports up to 10pcs parallel with master-slave control, which saves time and money on the installation and provides higher stability. In the parallel system, all batteries connected to different inverters are always kept at the same SOC level no matter how diversified the loads are connected with each inverter.
Parallel Solution
Master-Slave Control Parallel System

## Slide 3
Notice Before Use
Only a smart meter and a group of CTs are required for a parallel system.
Inverters in the parallel system should be the same model, and battery as well.
On-grid inverter cannot be involved in a paralleled hybrid system.
Battery cannot be connected in parallel, one battery rack connects to one inverter.
A slave inverter in a parallel system that loses CAN bus communication won't affect the whole system's operation, just the inverter that lost communication will stop working. However, if a master inverter in a parallel system loses contact with the Smart Meter, the entire system will fail.
In the parallel system, each battery connected in the system can reach a fully charged status or discharge to a specific SOC value almost at the same time.
In the parallel system, the settings of the master inverter will automatically sync to all slave inverters which means you just need to set the parameter of the system once.
Master-Slave Control Parallel System

## Slide 4
Normal 3Phase Load
Grid
Back-up Load
RS485
CAN
Meter
CT*3
Battery
PV
CAN
On-grid
Back-up
On-grid
Back-up
Battery
PV
CAN
MAX. 10pcs
Master Inverter
Slave Inverter N
1Phase Load
Back-up Load
Parallel System-Whole System Wiring Diagram

## Slide 5
CAN
CAN
Master Inverter
Slave Inverter 1
Slave Inverter N
…
…
Parallel System-CAN Communication Illustration

## Slide 6
CAN
CAN
Turn the CAN terminating resistors of the Master and the last slave inverter to ON position.
Master Inverter
Slave Inverter 1
Slave Inverter N
Parallel System-CAN Communication Wiring
ON
ON
…

## Slide 7
CAN
CAN
Master Inverter
Slave Inverter 1
Slave Inverter N
One parallel system only needs one smart meter and it’s connected to the Master inverter.
RS485
Parallel System-Smart Meter Connection
…
RS485-2

## Slide 8
In Germany and some European countries, an inverter connected to the grid must be able to receive the grid dispatch instructions to feed the power to the grid as required, which we called the RCR function. The communications ports for the RCR device to connect are shown below;
Master Inverter
Only the master device needs to be connected.
Only integrated with active power adjusting function.
Parallel System-RCR Connection

## Slide 9
DI
4+
DI
4-
DI
3+
DI
3-
DI
2+
DI
2-
DI
1+
DI
1-
K4
K3
K2
K1
Ripple Control Receiver
Active Power Dry Contact Connection Diagram
When K1 is turned on, the maximum allowed feed-in power is 100% of the total rated power of the inverter.
When K2 is turned on, the maximum allowed feed-in power is 60% of the total rated power of the inverter.
When K3 is turned on, the maximum allowed feed-in power is 30% of the total rated power of the inverter.
When K4 is turned on, feed-in power is not allowed.
The RCR function must be enabled on the inverter screen or the App. If the Ripple Control Receiver is not connected or the RCR function is not enabled, the inverter will fail to output.
Only the master inverter needs to connect to the Ripple Control Receiver in a parallel system.
Parallel System-RCR Connection
Notes: In Germany and some European countries, an inverter connected to the grid must be able to obey the grid dispatch instructions to feed the power to the grid as required, which we called the RCR function. The interface of this function is as follows;

## Slide 10
Install the parallel system according to the system wiring diagram, especially the CAN communication between each inverter.
Each inverter has to equip with a WiFi/LAN dongle.
Batteries need to connect to each inverter separately.
Power on all the inverters (Don’t turn on the backup loads before the parallel system commissioning is completed.)
  If there is a power grid connection, connect the inverter to the power grid.
  If there is no power grid, switch on the battery and PV.
Configure the WIFI network for the whole system.
Create a power plant in the SOLINTEG monitoring platform and add all inverters in the plant.
Set the inverter connected to the smart meter as the Master via the monitoring platform (or the screen) and set other inverters as Slave by the same mean, turn on the terminal resistor of the Master and last Slave inverter.
Confirm that all inverters are online in the monitoring platform.
Set the necessary parameters of the master inverter via APP or screen, such as safety code, export limit, RRCR, etc.
All inverters are connected to the power grid, batteries and PV to make sure that the system can run normally.
When the parallel system runs properly, turn on the loads connected to the backup side.
Parallel System-Operation Procedures
Notes: 全部图片待替换

## Slide 11
Advanced
Settings
InPut Password
1000
Verify OK
Verify Fail
<Advanced>
Multi-INV Role
Slave
<Advanced>
Multi-INV Role
Slave
<Advanced>
Multi-INV Role
Master
1s
1s
1s
1s
Wait
Wait
Correct
Incorrect
1s
…
1s
Parallel System-Inverter Role Setting
<Advanced>
Multi-INV Role
Master
<Advanced>
Multi-INV Role
Slave
Inverter Screen Settings
Inverter App Settings

## Slide 12
Wattsonic Cloud Setting
Set each inverter’s role in a parallel system in the Web portal. Click [Management], [Device Management],[ ], [Feature Parameters], [Multiple Inverter Role] to set or change the inverter role.
Parallel System-Inverter Role Setting
Web Portal Settings

## Slide 13
Wattsonic Cloud Setting
Login Solinteg cloud @ https://www.solinteg-cloud.com and click [Plant Management]—[Add Plant].
Parallel System-Create A Parallel Plant in Solinteg Monitoring

## Slide 14
Wattsonic Cloud Setting
Fill in the required fields which are marked with * in Installation Info and Location menu.
Parallel System-Create A Parallel Plant in Solinteg Monitoring

## Slide 15
Once one device information from the paralleling system is filled in, the others in this parallel system will automatically pop up. Click [Batch] to add all the inverters. (Please remember to set the inverter’s role as Master or Slave via the inverter screen or SolintegSet APP).
Note: The inverter connected with Smart Meter must be set as Master inverter.
Wattsonic Cloud Setting
Parallel System-Create A Parallel Plant in Solinteg Monitoring

## Slide 16
Wattsonic Cloud Setting
Input the electricity price and select currency according to the local policy. Click the [Complete] button, and a notice of creating plant successfully will pop up.
Parallel System-Create A Parallel Plant in Solinteg Monitoring

## Slide 17
Wattsonic Cloud Setting
Login Solinteg cloud , enter [Device Management] menu, and then click [Add Device].
Parallel System-Add Device to An Existing Plant

## Slide 18
Once one device information from the paralleling system is filled in, the others in this parallel system will automatically pop up. Click [Batch] to add all the inverters. (Please remember to set the inverter’s role as Master or Slave via the inverter screen or SolintegSet APP).
Note: The inverter connected with Smart Meter must be set as Master inverter.
Wattsonic Cloud Setting
Parallel System-Add Device to An Existing Plant

## Slide 19
THANK YOU
www.solinteg.com