## Slide 1
SOLINTEG DIESEL GENERATOR CONNECTION SOLUTION
www.solinteg.com
Solinteg Diesel Generator Connection Solution
academy@solinteg.com

## Slide 2
Brief Introduction
Why do we need a diesel generator in a PV system?
A diesel generator is used in a PV system as a backup power source to ensure a continuous power supply in case of a long - time grid power failure or insufficient power generation. Currently, Solinteg 25-50kW inverters support connecting the diesel generator to provide full backup for your energy security. And it can automatically start the generator when other power sources are insufficient.
www.solinteg.com
Solinteg Diesel Generator Connection Solution
02
academy@solinteg.com
Friendly
Reliable
Ensure the energy security for your critical loads when the power grid goes off for a long period.
Intelligent
Operate your diesel generator remotely and automatically
Integrate the control strategy and DG connector inside the inverter,
no need for any extra configuration.
Notes: 创新型去中心化解决方案
传统的工商业方案：并离网逆变器+并离网切换柜+PCS+EMS；
旧：受限多 防护等级低，仅能室外安装并须加装防护设施；复杂性 系统设备多安装运维复杂，协同性差；不稳定 设备运维复杂，系统可靠性降低；成本高 设备多，安装、运输及运维成本高；效率低 协同性低、设备间能源损耗高，系统效率低
新：灵活化 IP65 保护等级，满足室内和室外安装要求；一体化 一体化控制器，开发协同性好，性能强；高可靠 得益于魔睿开发平台的模块化设计理念；成本低 易运输, 产品运维成本低；效率高 多电平拓扑，新一代半导体器件，系统效率高

## Slide 3
www.solinteg.com
Solinteg Diesel Generator Connection Solution
03
academy@solinteg.com
No grid
Geological disasters
Island
Frequent
power outages
Application
Who will need this
With this function it would be easier to handle these situations:
Isolated areas without grid;
Regions with frequent geological disasters, such as earthquakes, typhoons, etc;
Places with frequent power outages;
Island or remote regions;
......

## Slide 4
Strategy
Solinteg DG strategy
www.solinteg.com
Solinteg Diesel Generator Connection Solution
04
academy@solinteg.com
Solinteg DG solution has been divided into three stages*, and each stage will be developed independently.
Stage 1: Use the DG to power home loads automatically when the power grid fails and PV and battery power is insufficient.
Stage 2: Use the DG to power loads and charge the battery.
Step 3: In addition to the functions of stage 1&2, you can use the DG as the grid, allowing you to run a microgrid in isolation.
*Note: We have completed the development of stage 1. For more information about the status of stage 2&3, please consult us. The remaining details will be released before Q4 2024.
Power the loads by DG automatically
Charge the battery
Act as the grid

## Slide 5
Connection
How to wire
www.solinteg.com
Solinteg Diesel Generator Connection Solution
05
academy@solinteg.com
As the diagram shown on the left:
Connect the DG controller to the COM3 Pin 11&12;
Connect the DG controller to the DG;*
Connect the output of DG to the inverter GEN port;
Connect the battery, back-up loads and other necessary devices;
*: The connection between DG and DG controller please refer to the user manual of the controller manufacture strictly.
Battery
DG
Grid
On-grid load
Back-up load
DG controller

## Slide 6
Logic
How it works
www.solinteg.com
Solinteg Diesel Generator Connection Solution
06
academy@solinteg.com
When the grid fails and is not recovered:
Point 1: Grid outages occur.
Point 2: PV power is lower than Pload, and the battery starts to discharge.
Point 3: The battery State of Charge (SOC) drops to 25%, and the DG enters standby status.
Point 4: If SOC is lower than 20% or remains lower than 25% for over 10 minutes, the inverter will switch the loads to be powered by the DG.
Point 5: When PV power recovers, the battery starts to charge.
Point 6: Once SOC recovers to 50%, the inverter begins detecting the battery status.
Point 7: If SOC remains higher than 50% for over 5 minutes, the inverter switches the loads back to be powered by the battery and PV, then closes the DG.
Point 8: PV power is higher than Pload.
Battery SOC
PLoad
PV Power
Grid Outage
20
25
50
2
3
4
5
7
8
DG Start
10 minutes maximum
1
6
DG Working
Checking
DG Off
5 minutes
PV
PV+Battery
DG
Load Consumption Source
SOC
P
T

## Slide 7
Logic
How it works
www.solinteg.com
Solinteg Diesel Generator Connection Solution
07
academy@solinteg.com
Battery SOC
PLoad
PV Power
Grid Outage
20
25
2
3
4
5
7
8
DG Start
10 minutes maximum
1
6
DG Working
Grid Recovered
DG Off
5 minutes
PV
PV+Battery
DG
Load Consumption Source
Grid+PV
SOC
P
T
When the grid fails and is recovered after a while:
Point 1: Grid outages occur.
Point 2: PV power is lower than Pload, and the battery starts to discharge.
Point 3: The battery State of Charge (SOC) drops to 25%, and the DG enters standby status.
Point 4: If SOC is lower than 20% or remains lower than 25% for over 10 minutes, the inverter will switch the loads to be powered by the DG.
Point 5: When PV power recovers, the battery starts to charge.
Point 6: Once the grid is recovered, the inverter begins detecting the grid status.
Point 7: If the grid is stable for over 5 minutes, the inverter switches the loads back to be powered by the grid and PV, then closes the DG.
Point 8: PV power is higher than Pload.
The power dispatching order priority is related to the inverter work mode.

## Slide 8
Requirements
How to select the devices
www.solinteg.com
Solinteg Diesel Generator Connection Solution
08
academy@solinteg.com
All the devices selected just as the recommendation;
*: For the firmware upgrade please contact us at service@solinteg-power.com;
**: Please make sure the DG controller has the DO input port before you purchase it;
***: Please make sure the DG supports the connection with the controller you purchased;
DG output: The output power parameter we take a 50kW inverter as an example. Solinteg 50kW inverter max DG input apparent power is 60kW, so the DG’s rated output power should be within 60kW;
For more parameters, please refer to the inverter datasheet.
Requirements
Inverter
DG Controller
DG
MHT 25-50K
(Special firmware is needed, please contact us.)*
DO input port integrated**
1. DG controller connection available；
2. Three phase DG only;
3. Output power within the limitation of the inverter***；
Products
Requirements

## Slide 9
www.solinteg.com
Solinteg Diesel Generator Connection Solution
END
academy@solinteg.com
END
Visit Solinteg website to find out more
Notes: 1. 尽量讲全；
2. 自信；
3.